## WR
TYPIQUE | SYMBOLE | NOM FOLIO | Tag N° | #REF! | Desc 1 | Desc 2 | Chassis | #REF! | #REF! | #REF! | #REF! | #REF! | SPARE | Carte | Type de Carte | Borne carte1 | Borne carte2 | Cable Connection | #REF! | Type de platine | Borne Platine IN | Borne Platine IN2 | PLATINE BORNE OUT 1 | PLATINE BORNE OUT 2 | PLATINE BORNE OUT 3 | PLATINE BORNE OUT 3 | PLATINE REPERE CABLE OUT 1 Fils + | PLATINE REPERE CABLE OUT 2 Fils - | PLATINE REPERE CABLE OUT 3 Fils comm | PLATINE REPERE CABLE OUT 3 Alim 24VDC | ARMOIRE BORNIER IMAGE | ARMOIRE BORNIER 1 | ARMOIRE BORNIER 2 | ARMOIRE BORNIER 3 | ARMOIRE BORNIER 4 | SPARE | MULTICABLE REPERE | MULTICABLE TYPE | Repère connect. |  |  | SPARE | BJ REPERE | BJ Borne 1 | BJ Borne 2 | BJ Borne 3 | BJ Borne 4 | SPARE | SPARE | CABLE INSTRUM. REPERE | CABLE INSTRUM. TYPE | CABLE INSTR. Repère connect. |  | SPARE | SPARE | ARMOIRE REPERE | AUTOMATE REF DOC | AUTOMATE N° FOLIO | BORNIER IMAGE REF DOC | BORNIER IMAGE N° FOLIO | BJ REF DOC | BJ N° FOLIO | DRAWING BY |  |  |  | CHECKED BY |  |  |  | APPROVED BY
A3 - BOUCLE ANA [1AI PASSIF] | AI | OMB_LT4004 | LT4004 | OMB_LT4004 | Oil Level D700 |  | Chassis P3 | P | 3 | 5 | 15 | AI |  | P3.5-AI03 | 1756-IF16 | 36 |  | L3AI03 | P3AI03 | 1492-AIFM16-F-5 | 21 |  | TB2-B9 | TB2-C8 | TB2-C16 |  | 3.5.15/+V15 | 3.5.15/IN15 |  |  | MA-BJ4000-AI | 1 | 2 |  |  |  | IBJ4000-AI | 19IP09EGFA | RD | WH |  |  | BJ4000-AI | 1 | 2 |  |  |  |  | ILT4004 | 01IP09EGFA | RD | WH |  |  | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 65 | GAB-OBA-402-RA-DW-J-102 | FOLIO 156 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
A3 - BOUCLE ANA [1AI-1AO] | AI | OMB_FT7020A | FT7020A | OMB_FT7020A | Mini Flow OIL TRANSFER | PUMPS P702A | Chassis P3 | P | 3 | 8 | 0 | AI |  | P3.8-AI06 | 1756-IF16 | 2 |  | L3AI06 | P3AI06 | 1492-AIFM16-F-5 | 3 |  | TB1-B2 | TB1-C1 | TB1-C9 |  | 3.8.0/+V0 | 3.8.0/IN0 |  |  | MA-BJ7000-AI | 13 | 14 |  |  |  | IBJ7000-AI | 19IP09EGFA | RD | WH |  |  | BJ7000-AI | 13 | 14 |  |  |  |  | IFT7020A | 01IP09EGFA | RD | WH |  |  | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 70 | GAB-OBA-402-RA-DW-J-102 | FOLIO 158 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
§SUITE | AO_VANNE | OMB_FV7020 A | FV7020 A | OMB_FV7020 A | FCV Mini Flow OIL TRANSFER | PUMPS P702A | Chassis P3 | P | 3 | 13 | 5 | AO |  | P3.13-AO03 | 1756-OF8 | 10 | 6 | L3AO03 | P3AO03 | 1492-AIFM8-3 | 25 | 24 | B11 | B12 |  |  | 3.13.5/OUT5 | 3.13.5/RTN |  |  | MA-BJ7000-AO | 1 | 2 |  |  |  | IBJ7000-AO | 12IP09EGFA | RD | WH |  |  | BJ7000-AO | 1 | 2 |  |  |  |  | IFV7020 A | 01IP09EGFA | RD | WH |  |  | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 78 | GAB-OBA-402-RA-DW-J-102 | FOLIO 160 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
A3 - BOUCLE ANA [1AO] | AO | OMB_PY7005A | PY7005A | OMB_PY7005A | PCV Minimum flow P700A to D201 |  | Chassis P3 | P | 3 | 11 | 1 | AO |  | P3.11-AO01 | 1756-OF8 | 9 | 5 | L3AO01 | P3AO01 | 1492-AIFM8-3 | 1 | 14 | B3 | B4 |  |  | 3.11.1/OUT1 | 3.11.1/RTN |  |  | MA-BJ7005-AO | 1 | 2 |  |  |  | IBJ7005-AO | 12IP09EGFA | RD | WH |  |  | BJ7005-AO | 1 | 2 |  |  |  |  | IPY7005A | 01IP09EGFA | RD | WH |  |  | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 76 | GAB-OBA-402-RA-DW-J-102 | FOLIO 161 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
A3 - BOUCLE ANA [1AI ACTIF] | AI_P | OMB_FD0021 | FD0021 | OMB_FD0021 | Fire detector | WATER INJECTION PUMPS | Chassis P3 | P | 3 | 9 | 13 | AI |  | P3.9-AI07 | 1756-IF16 | 32 |  | L3AI07 | P3AI07 | 1492-AIFM16-F-5 | 22 |  | TB2-B7 | TB2-C6 | TB2-C14 |  | 3.9.13/+V13 | 3.9.13/IN13 | 3.9.13/RTN | 06D1/+ | MAF-FD0021 | 1 | 2 | 3 |  |  | IFD0021 | 01IT09EGFAFR | RD | WH | BU | [14 empty] | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 73 | GAB-OBA-402-RA-DW-J-102 | FOLIO 184 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
A3 - BOUCLE DIG [SOV+2FDC] | SOV | OMB_SOV1413 | SOV1413 | OMB_SOV1413 | SDV4010 to Water | Injection Manifold | Chassis P3 | P | 3 | 15 | 13 | DO |  | P3.15-DO01 | 1756-OB32 | 14 |  | L3DO01 | P3DO01.1 | 1492-XIM4024-16RF | 31 |  | TB2-16 | TB2-17 | TB2-18 |  |  | 06D1/+ | 3.15.13/NO13 | 06D1/- | MD-BJ4010-DO | 3 | 4 |  |  |  | IBJ4010-DO | 12x1,5 U1000RVFV |  |  |  |  | BJ4010-DO | 3 | 4 |  |  |  |  | ISOV1413 | 3G1,5 U1000RVFV |  |  |  |  | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 81 | GAB-OBA-402-RA-DW-J-102 | FOLIO 154 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
§SUITE | ZSH | OMB_ZSH1413 | ZSH1413 | OMB_ZSH1413 | LSO SDV4010 to | Water Injection Manifold | Chassis P3 | P | 3 | 1 | 26 | DI |  | P3.1-DI01 | 1756-IB32 | 29 |  | L3DI01 | P3DI01 | 1492-IFM40D24A-2 | 26 |  | A34 | B33 |  |  | 3.1.26/+V1 | 3.1.26/IN26 |  |  | MD-BJ4010-DI | 1 | 2 |  |  |  | IBJ4010-DI | 12IP09EGFA | RD | WH |  |  | BJ4010-DI | 1 | 2 |  |  |  |  | IZSH1413 | 01IQ09EGFA |  |  |  |  | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 55 | GAB-OBA-402-RA-DW-J-102 | FOLIO 152 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
§SUITE | ZSL | OMB_ZSL1413 | ZSL1413 | OMB_ZSL1413 | LSC SDV4010 to | Water Injection Manifold | Chassis P3 | P | 3 | 1 | 27 | DI |  | P3.1-DI01 | 1756-IB32 | 30 |  | L3DI01 | P3DI01 | 1492-IFM40D24A-2 | 28 |  | A35 | B34 |  |  | 3.1.27/+V1 | 3.1.27/IN27 |  |  | MD-BJ4010-DI | 3 | 4 |  |  |  | IBJ4010-DI | 12IP09EGFA | RD | WH |  |  | BJ4010-DI | 3 | 4 |  |  |  |  | IZSL1413 | 01IQ09EGFA |  |  |  |  | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 55 | GAB-OBA-402-RA-DW-J-102 | FOLIO 152 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
A3 - BOUCLE DI_CMD | DI_CMD | OMB_MXS700C | MXS700C | OMB_MXS700C | Running Status | Export Pump P700C | Chassis P3 | P | 3 | 2 | 1 | DI |  | P3.2-DI02 | 1756-IB32 | 2 |  | L3DI02 | P3DI02 | 1492-IFM40D24A-2 | 7 |  | A3 | B4 |  |  | 3.2.1/+V0 | 3.2.1/IN1 |  |  | MD-BJ700C-DI | 3 | 4 | [16 empty] | IMXS700C | [5 empty] | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 56 | GAB-OBA-402-RA-DW-J-102 | FOLIO 189 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
A3 - BOUCLE DO_CMD | DO_CMD | OMB_MXH700C | MXH700C | OMB_MXH700C | Run Command | Export Pump P700C | Chassis P3 | P | 3 | 15 | 4 | DO |  | P3.15-DO01 | 1756-OB32 | 5 |  | L3DO01 | P3DO01.1 | 1492-XIM4024-16RF | 13 |  | TB1-15 | TB1-16 | TB1-17 |  |  | 3.15.4/COM | 3.15.4/OUT4 | 06D1/- | MD-BJ700C-DO | 1 | 2 | [22 empty] | GAB-OBA-402 - DCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 80 | GAB-OBA-402-RA-DW-J-102 | FOLIO 190 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
A3 - BOUCLE DI_PDCS | DI_PDCS | DI_OMB_SW501_QG_TRIPPED | SW501_QG_TRIPPED | DI_OMB_SW501_QG_TRIPPED | Incomming QG CB Open/Tripped |  | PDCS 2 | R | 2 | 1 | 3 | DI |  | R2.1-DI01 | 1756-IB16ISOE | 8 | 7 | L2DI01 | P2DI01 | 1492-IFM40DS24A-4 | 11 | 12 | A7 | A8 | B12 | B4 | 07D1/+ | 2.1.3/+V3 | 2.1.3/IN3 | 07D1/- | SW204-DI | 7 | 8 | [22 empty] | GAB-OBA-402 -PDCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 102 | GAB-OBA-402-RA-DW-J-102 | FOLIO 212 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
A3 - BOUCLE DO_PDCS | DO_PDCS | DO_OMB_SW501_QG_CL_ORDER | SW501_QG_CL_ORDER | DO_OMB_SW501_QG_CL_ORDER | Remote (PDCS) CLOSE Order |  | PDCS 2 | R | 2 | 3 | 0 | DO |  | R2.3-DO01 | 1756-OB32 | 1 |  | L2DO01 | P2DO01.1 | 1492-XIM4024-16RF | 5 |  | TB1-3 | TB1-4 | TB1-5 |  |  | 2.3.0/COM0 | 2.3.0/OUT0 |  | SW204-DO | 1 | 2 | [22 empty] | GAB-OBA-402 -PDCS | GAB-OBA-402-RA-DW-J-102 | FOLIO 106 | GAB-OBA-402-RA-DW-J-102 | FOLIO 213 | A définir par le client |  | FPL | A | 2015-02-19 | PREMIERE EMISSION | YGO | A | 2015-02-19 | PREMIERE EMISSION | API | A | 2015-02-19 | PREMIERE EMISSION
§FIN